OBRAZAC 1  

Crnogorski elektroprenosni sistem AD Podgorica

Broj iz evidencije postupaka javnih nabavki: 77/24
Redni broj iz Plana javnih nabavki: 38
Mjesto i datum: Podgorica, 16.12. 2024. godine
Na osnovu člana 53 stav 3 Zakona o javnim nabavkama („Službeni list CG“, br. 74/19, 3/23 i 11/23) Crnogorski elektroprenosni sistem AD Podgorica objavljuje        

TENDERSKU DOKUMENTACIJU

ZA OTVORENI POSTUPAK JAVNE NABAVKE:
Revitalizacija rasvjete i elektroinstalacija u trafostanicama
Predmet nabavke se nabavlja kao cjelina.

1. POZIV ZA NADMETANJE 

1. Podaci o naručiocu;

2. Podaci o postupku i predmetu javne nabavke: 

2.1. Vrsta postupka,

2.2. Predmet javne nabavke (vrsta predmeta, naziv i opis predmeta),

2.3. Procijenjena vrijednost predmeta nabavke

2.4. Način nabavke: 

· Cjelina, po partijama,

· Zajednička nabavka,

· Centralizovana nabavka,

2.5. Posebni oblik nabavke:

· Okvirni sporazum,

· Dinamički sistem nabavki,

· Elektronska aukcija,

· Elektronski katalog,

2.6. Uslovi za učešće u postupku javne nabavke i posebni osnovi za isključenje,

2.7. Kriterijum za izbor najpovoljnije ponude,

2.8. Način, mjesto i vrijeme podnošenja ponuda i otvaranja ponuda,

2.9. Rok za donošenje odluke o izboru,

2.10. Rok važenja ponude,

2.11. Garancija ponude

2. TEHNIČKA SPECIFIKACIJA PREDMETA JAVNE NABAVKE

1. Naziv i opis predmeta nabavke u cjelini, po partijama i stavkama sa bitnim karakteristikama

2. Zahtjevi u pogledu načina izvršavanja predmeta nabavke koji su od značaja za sačinjavanje ponude i izvršenje ugovora

3. DODATNE INFORMACIJE O PREDMETU I POSTUPKU NABAVKE

Sa ponuđačem sa kojim bude zaključen ugovor o javnoj nabavci, Naručilac će zaključiti i Ugovor o organizovanju i sprovođenju mjera zaštite i zdravlja na radu, međusobnim pravima, obavezama i odgovornostima
Dio radova moguće je izvoditi jedino u beznaponskom stanju. Obaveza Izvođača je da radove za koje je potrebno beznaponsko stanje izvodi u terminima beznaponskog stanja koje obezbijedi Naručilac, a sve u zavisnosti od stanja u elektroenergetskom sistemu u datom trenutku. Naručilac radova je u obavezi da obezbijedi beznaponsko stanje i da javi Izvođaču radova sedam dana prije početka beznaponskog stanja. 

Izabrani ponuđač je dužan da dostavljeni ugovor potpiše i vrati Naručiocu zajedno sa avansnom garancijom i garancijom za dobro izvršenje ugovora u roku od 15 dana od dana dostavljanja ugovora.
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Procijenjena vrijednost predmenta nabavke:

(  Procijenjena vrijednost predmeta nabavke bez zaključivanja okvirnog sporazuma:
(  kao cjeline je 70.000,00 €
Obrazloženje razloga zašto predmet nabavke nije podijeljen na partije:
Predmet javne nabavke predstavlja tehničko-tehnološku cjelinu, te stoga nije podijeljen po partijama. 

PONUDA SA VARIJANTAMA

Mogućnost podnošenja ponude sa varijantama
( Varijante ponude nijesu dozvoljene i neće biti razmatrane.

REZERVISANA NABAVKA
( Ne

4. NAČIN UTVRĐIVANJA EKVIVALENTNOSTI

Način utvrđivanja ekvivalentnosti: nije primjenjivo
5. OSNOVI ZA OBAVEZNO ISKLJUČENJE IZ POSTUPKA JAVNE NABAVKE

Privredni subjekat će se isključiti iz postupka javne nabavke, ako: 

1) je vršio neprimjeren uticaj u smislu člana 38 stav 2 tačka 1 ovog zakona;

2) postoji sukob interesa iz člana 41 stav 1 tačka 2 ili člana 42 ovog zakona;

3) ne ispunjava uslov iz člana 99 ovog zakona;

4) ne ispunjava uslov iz čl. 102, 104 ili 106 ovog zakona predviđen tenderskom dokumentacijom;

5) nije dostavio izjavu privrednog subjekta ili dostavljena izjava ne sadrži informacije i podatke tražene tenderskom dokumentacijom ili je nepravilno sačinjena;

6) postoji razlog na osnovu kojeg se smatra da je odustao od prijave, odnosno ponude, a koji je propisan članom 120 stav 15 ovog zakona;

7) nije dostavio garanciju ponude ili nije dostavio garanciju ponude na način predviđen tenderskom dokumentacijom u skladu sa članom 122 st. 2, 3 ili 4 ovog zakona ili je dostavio garanciju ponude na manji iznos od traženog ili je ta garancija neispravna; i/ili

8) postoji drugi razlog propisan ovim zakonom.
6. SREDSTVA FINANSIJSKOG OBEZBJEĐENJA UGOVORA O JAVNOJ NABAVCI

Ponuđač čija ponuda bude izabrana kao najpovoljnija je dužan da uz potpisan ugovor o javnoj nabavci dostavi naručiocu:

- Ponuđač čija ponuda bude izabrana kao najpovoljnija je dužan da uz potpisan ugovor o nabavci dostavi naručiocu bezuslovnu i na prvi poziv naplativu garanciju za povrat primljenog avansa na iznos vrijednosti avansa, sa rokom važenja 30 dana dužim od roka izvršenja ugovora.
- garanciju za dobro izvršenje ugovora, za slučaj povrede ugovornih obaveza u iznosu od 10% od ukupne vrijednosti ugovora sa PDV-om i sa rokom važenja 30 dana dužim od roka izvršenja ugovora, kojom bezuslovno i neopozivo garantuje potpuno i savjesno izvršenje ugovorenih obaveza. Ukoliko se primopredaja radova ne izvrši najkasnije 15 (petnaest) dana prije isteka važnosti garancije za dobro izvršenje ugovora kao i u slučaju izvjesnog prekoračenja roka izvođenja radova, Izvođač je dužan da produži rok važenja garancije za dobro izvršenje ugovora najkasnije 10 dana prije njenog isticanja za period od 30 (trideset) dana duži od produženog roka za izvođenje radova. Ukoliko izvođač blagovremeno ne produži garanciju u ostavljenom roku naručilac će aktivirati garanciju koja je na snazi i jednostrano raskinuti ugovor. 
7. METODOLOGIJA VREDNOVANJA PONUDA

Naručilac će u postupku javne nabavki izabrati ekonomski najpovoljniju ponudu, primjenom pristupa isplativosti, po osnovu kriterijuma: 

(odnos cijene i kvaliteta 
1. Ponude po parametru cijena vrednovaće se na sledeći način: 

Maksimalan broj bodova po ovom potkriterijumu je 70
Broj bodova po potkriterijumu cijena određuje se po formuli:

C= (Cmin/Cp)x70,
gdje je:

C – broj bodova za ponuđenu cijenu,

         Cmin – najniža ponuđena cijena (bez PDV-a),

Cp –  ponuđena cijena (bez PDV-a),

70 – maksimalni broj bodova po ovom potkriterijumu.   

2. Ponude po parametru kvalitet vrednovaće se na sledeći način: 

Kvalitet ponude se provjerava u 3 parametra i to: 

· Najmanja ukupna instalisana snaga svjetiljki – maksimalno 10 bodova

· Najmanja instalisana snaga svjetiljki u Zoni 1 – maksimalno 15 bodova

· Najduža garancija na svjetiljke – maksimalno 5 podova
Dodjela bodova se vrši na sledeći način: Najbolje rangirani u pojedinačnom kriterijumu dobija maksimalni broj bodova za taj kriterijum. Ostali ponuđači dobijaju bodove procentualno u odnosu na rezultat najbolje rangiranog, po svakoj stavki kriterijuma zasebno. 
Matematička formula bodovanja po kriterijumu glasi: 
A = Ar/Br*Mp gdje je A osvojeni broj bodova u kriterijumu, Ar je rezultat ponude, Br je je rezultat ponude prvorangiranog u tom kriterijumu a Mp je maximalni broj bodova za taj kriterijum. Zatim se bodovi po svim kriterijumima sabiraju i čine ukupni broj poena ponude. 
Ponuđač koji bude imao najveći broj bodova zbirom oba potkriterijuma biće izabran kao najpovoljniji.
8. JEZIK PONUDE

Ponuda se sačinjava na:

( crnogorski jezik i drugi jezik koji je u službenoj upotrebi u Crnoj Gori, u skladu sa Ustavom i zakonom
9. NAČIN, MJESTO I VRIJEME PODNOŠENJA PONUDA I OTVARANJA PONUDA

Ponude se podnose preko ESJN-a zaključno sa danom 21.01.2025. godine do 08:00 sati.

Otvaranje ponuda održaće se dana 21.01.2025. godine u 08:00  sati. 

( U skladu sa članom 122 Zakona o javnim nabavkama, garancija ponude podnosi se u elektronskom obliku putem ESJN.

Izuzetno, ako ponuđač ne može da garanciju ponude podnese u elektronskom obliku, dužan je da putem ESJN dostavi kopiju garancije ponude, a da original garancije ponude dostavi, odnosno uruči naručiocu neposredno ili putem pošte, preporučenom pošiljkom najkasnije prije isteka roka za podnošenje ponuda.

( Dio ponude koje se ne dostavlja preko ESJN-a, a odnosi se na garanciju ponude dostavlja se: 

· neposrednom predajom na arhivi naručioca na adresi ul. Bulevar Svetog Petra Cetinjskog 18, Podgorica;

· preporučenom pošiljkom sa povratnicom na adresi ul. Bulevar Svetog Petra Cetinjskog 18, Podgorica;

radnim danima od 08:00 do 15:00 sati, zaključno sa danom 21.01.2025. godine do 08:00 sati.

Napomena: U ovom slučaju, original garancije ponude u pisanom obliku se dostavlja u koverti, na kojoj se navodi: naziv i sjedište naručioca, broj tenderske dokumentacije za koju se podnosi garancija, naziv, sjedište i adresa ponuđača i naznake "garancija ponude" i "ne otvaraj prije roka za otvaranje ponuda". 
10. USLOVI ZA AKTIVIRANJE GARANCIJE PONUDE

Garancija ponude će se aktivirati ako ponuđač: 

     1) odustane od ponude u roku važenja ponude i/ili

2) odbije da zaključi ugovor o javnoj nabavci.

11. TAJNOST PODATAKA

Tenderska dokumentacija sadrži tajne podatke

( ne

12. UPUTSTVO ZA SAČINJAVANJE PONUDE

Ponude se sačinjava u ESJN u skladu sa tenderskom dokumentacijom i važećim Pravilnikom o sadržaju ponude i uputstvu za sačinjavanje i podnošenje ponude. 

Ispunjenost uslova za učešće u postupku javne nabavke dokazuje se izjavom privrednog subjekta, koja se sačinjava na obrascu datom u Pravilniku o obrascu izjave privrednog subjekta.

Ponuđač je dužan da tačno, potpuno, pravilno i nedvosmisleno popuni Izjavu privrednog subjekta u skladu sa zahtjevima iz tenderske dokumentacije.
Ponuđač je dužan da u izjavi privrednog subjekta navede potpune, jasne i tačne podatke. U slučaju podnošenja zajedničke ponude, izjavu privrednog subjekta daje svaki član zajedničke ponude, a ako je ponuda podnijeta sa podugovaračem – i svaki podugovarač.

13. NAČIN ZAKLJUČIVANJA I IZMJENE UGOVORA O JAVNOJ NABAVCI

Naručilac zaključuje ugovor o javnoj nabavci u pisanom ili elektronskom obliku sa ponuđačem čija je ponuda izabrana kao najpovoljnija, nakon izvršnosti odluke o izboru najpovoljnije ponude. 

Ugovor o javnoj nabavci mora da bude u skladu sa uslovima utvrđenim tenderskom dokumentacijom, izabranom ponudom i odlukom o izboru najpovoljnije ponude, osim u pogledu iskazivanja PDV-a.

Ugovor između naručioca i ponuđača čija je ponuda izabrana kao najpovoljnija, pored uslova koji su propisani ovom tenderskom dokumentacijom, će sadržati i sljedeće:

· Po zaključenju ugovora prije izvođenja radova Izvođač je dužan dostaviti sledeću dokumentaciju:

· Tehničke listove nuđenih svjetiljki (koji potvrđuju podatke iz fotometrijskog proračuna kao i postojanje zasebnog SPD10kV uređaja u tijelu svjetiljke).

· ENEC sertifikate za svjetiljke iz ponude.

· Kataloške listove za opremu sklopne tehnike iz ponude (koji potvrđuju podatke iz ponude).

· Katalošku dokumentaciju za ormane iz ponude (koji potvrđuju podatke iz ponude).

· Radove je potrebno izvesti u svemu prema tehničkoj dokumentaciji, zakonskim propisima i pozitivnoj inženjerskoj praksi. 

· Nakon izvođenja svih radova, Izvođač je dužan izvršiti testiranje i puštanje u rad sistema rasvjete u prisustvu predstavnika Naručioca. Nakon puštanja u rad, Naručioc vrši mjerenje osvijetljenosti u pojedinim tačkama definisanim fotometrijskim proračunom u prisustvu Izvođača. Ukoliko do tada Naručioc ne prijavi uočene nedostatke, Izvođač pristupa sačinjavanju zapisnika o testiranju i mjerenjima, koji se obostrano potpisuje. Nakon toga, Izvođač je dužan izraditi projekat izvedenog stanja spoljne rasvjete, čijim predavanjem Naručiocu se stvaraju uslovi za primopredaju radova.   
Izvođač radova se obavezuje :

-  Da usluge pruža kvalifikovanom radnom snagom sa potrebnim licencama, znanjem i iskustvom za ovu vrstu posla.

-  Da primijeni mjere zaštite na radu propisane zakonom, kako ne bi došlo do povrede na poslu.

-  Da odmah, po zahtjevu predstavnika Naručioca, pristupi otklanjanju uočenih nedostataka i propusta u obavljanju posla.   
· Ponuđač može ponuditi drugačija rješenja rasvjete od rješenja datog u tehničkoj dokumentaciji, uz obavezno dostavljanje fotometrijskih proračuna u svemu izrađenim prema uslovima iz tehničke dokumentacije (na prilogu broj 18 - Podloga za fotometrijski proračun detaljno opisani kriterijumi i detalji za proračun, kao i u dijelu 5.3 tekstualnog dijela). Vrijednosti zadate u dokumentaciji i na prilozima su obavezujuće. Kao dokaz o ispunjenosti uslova, Ponuđač je u obavezi da dostavi fotometrijski proračun kojim se potkrepljuju podaci, a kojim se prikazuju svi parametri koji su dati u proračunu koji je sastavni dio tehničke dokumentacije. Uz proračun, Ponuđač je u obavezi da dostavi izvorni fotometrijski fajl iz kog je izveden proračun (EVO fajl na primjer), kako bi se provjerili detalji obrađenih elemenata, površina i tačaka. Za potrebe proračuna, Naručioc dostavlja Prilog br. 18 u izvornoj verziji (DWG fajl). Sve eventualne izmjene u količinama svjetiljki, nosača i kablova koje nastupe izmjenom rješenja rasvjete su odgovornost Ponuđača i eventualna uvećanja padaju na njegov trošak.

Prilikom izrade rješenja rasvjete i fotometrijskog proračuna, obavezno je pridržavanje sledećih kriterijuma i vrijednosti:

· Sve kalkulacijske površine se postavljaju na 0.02m visine.

· Svi objekti ucrtani na crtežu „Prilog 18“ moraju biti tretirani i u proračunu, sa njihovim visinama naznačenim na crtežu.

· "Maintenance factor" svjetiljki može biti maksimalno 0.9.

· Mrežu kalkulacijskih tačaka na površinama prilagoditi tačkama prikazanim na crtežu.

· Za kalkulacijske površine perimetra i pješačkih staza potrebno je imati isti broj tačaka kao na crtežu u oba smjera (isti „grid“). 

· Za kalkulacijske površine u postrojenjima, maksimalna udaljenost tačaka („grid“) je 2x3m (2m po užoj strani). 

· Visine svjetiljki na stubovima su u opsegu 25.0 - 25.8m (dno i vrh ograde). Iste je potrebno predvidjeti sa nosačem i podkonstrukcijom za montažu na stub/ogradu.

· Na portalima u 110kV postrojenju svjetiljke predvidjeti na maksimalno 9.5m.

· Maksimalna inklinacija reflektorskih svjetiljki na stubovima rasvjete je 65 stepeni u odnosu na horizontalnu ravan poda.

· Refleksije podnih površina maksimalno 20%.

· Refleksije zidova objekata maksimalno 50%.

· Zbog uticaja stubova portala u postrojenjima, iste je potrebno tretirati u proračunu. Zbog njihove rešetkaste prirode i uticaja na distribuciju svijetla, iste formirati kao "prozirne" (transparent) sa refleksijom ne većom od 50% (reflection factor) i  propustom ne većim od 40% (degree of transmission).

· Komplet rasvjetu postrojenja treba dizajnirati na način da postoje dva nivoa osvjetljaja, tj dvije zone paljenja.

· Zona 1, osnovni nivo ima sledeće potrebe u pogledu srednjeg nivoa osvjetljaja i ravnomjernosti: 

· Ulazna kapija - Em >20lx i Uo >0.4

· Ulazni koridor - Em >10lx i Uo >0.4

· Ostale Staze/Koridori - Em >10lx i Uo >0.2

· Perimetri - Em >5lx i Uo >0.2

· Transformatori (ETR) - Em >15lx i Uo >0.4

· Postrojenja (RP) 400kV i 110kV - Em > 20lx i Uo >0.2

· Zona 2, maksimalni nivo ima sledeće potrebe u pogledu srednjeg nivoa osvjetljaja i ravnomjernosti: 

· Ulazna kapija - Em >30lx i Uo >0.4

· Ulazni koridor - Em >20lx i Uo >0.4

· Ostale Staze/Koridori - Em >30lx i Uo >0.2

· Perimetri - Em >10lx i Uo >0.2

· Transformatori (ETR) - Em >50lx i Uo >0.4

· Postrojenja (RP) 400kV i 110kV - Em > 50lx i Uo >0.4

· Ponuda čiji fotometrijski proračun ne zadovoljava gore popisane kriterijume i vrijednosti smatraće se neispravnom i neće biti uzeta u razmatranje.

· Montaža svjetiljki se dozvoljava samo na postojećim stubovima rasvjete, portalima i fasadi objekta.

Izvođač je dužan da bez nadoknade u ugovorenom garantnom roku izvede radove kojim se otklanjaju nedostaci na predmetnom objektu. 
Ako Izvođač svojom krivicom ne završi predmetne radove u ugovorenom roku, dužan je da Naručiocu plati na ime ugovorene kazne penale 2‰ (promila) od ugovorene cijene svih radova za svaki dan prekoračenja ugovorenog roka završetka radova. Visina ugovorene kazne ne može preći 10% od ugovorene cijene radova. Ako Naručiocu nastane šteta zbog prekoračenja ugovorenog roka završetka radova u iznosu većem od ugovorene i obračunate kazne, tada Naručilac ima pravo i na naknadu štete u iznosu koji prelazi visinu ugovorene kazne.

Ukoliko dođe do raskida Ugovora i prekida radova, Izvođač je dužan da preduzme potrebne mjere da se izvedeni radovi zaštite od propadanja. Troškove zaštite radova snosi ugovorna strana čijom krivicom je došlo do raskida Ugovora odnosno do prekida radova.

Naručilac i Izvođač su saglasni da sastavni dio ugovora čine:

- ponuda Izvođača,

- sredstva finansijskog obezbjeđenja ugovora.
Na sve što nije regulisano odredbama ugovora, primijeniće se odredbe Zakona o obligacionim odnosima („Sl. list Crne Gore“, broj 47/08, 4/11, 22/17) koje su primjenljive i odnose se na ugovor o izvođenju radova.

Ugovorne strane su saglasne da sve eventualne sporove rješavaju sporazumno, u suprotnom spor će rešavati nadležni sud u Podgorici.

Ugovor o javnoj nabavci koji je zaključen uz kršenje antikorupcijskog pravila u skladu sa odredbama člana 38 ZJN (Sl.list Crne Gore br. 74/19,3/23 i 11/23) ništav je.

Ugovor o javnoj nabavci tokom njegovog trajanja može da se izmijeni bez sprovođenja novog postupka javne nabavke u skladu sa članom 151 Zakona o javnim nabavkama:

- ako su izmjene, bez obzira na njihovu vrijednost izraženu u novcu, predviđene tenderskom dokumentacijom i ugovorom o javnoj nabavci i uključuju izmjenu cijene, sa utvrđenim obimom i prirodom mogućih izmjena kao i uslovima u kojima se izmjene mogu vršiti, pod uslovom da se ugovorom ne predviđaju izmjene kojima se mijenja ukupna priroda ugovora o javnoj nabavci, a povećanje vrijednosti ugovora nije veće od 20% vrijednosti prvobitnog ugovora;

- radi nabavke dodatnih radova koji su postali neophodni, a koji nijesu bili uključeni u prvobitni ugovor o javnoj nabavci, ako promjena privrednog subjekta sa kojim je zaključen ugovor nije moguća iz ekonomskih ili tehničkih razloga, kao što su zahtjevi kompatibilnosti sa postojećIm radovima nabavljenim u okviru prvobitne nabavke i može da prouzrokuje značajne poteškoće ili znatno povećavanje troškova za naručioca a povećanje vrijednosti ugovora nije veće od 20% vrijednosti prvobitnog ugovora;
-kada je potreba za izmjenom ugovora nastala zbog okolnosti koje naručilac u vrijeme zaključivanja ugovora nije mogao da predvidi, a izmjenom se ne mijenja priroda ugovora a povećanje vrijednosti ugovora nije veće od 20% vrijednosti prvobitnog ugovora; 

-kad je potreba za izmjenom ugovora nastala zbog okolnosti koje naručilac u vrijeme zaključivanja ugovora nije mogao da predvidi, a izmjenom se ne mijenja priroda ugovora već se vrši samo smanjenje ugovorene vrijednosti, 

-kad se vrši zamjena podugovarača, u skladu sa članom 128 st. 10, 11 i 12 ovog zakona;

- ako privrednog subjekta nakon restrukturiranja, uključujući preuzimanje, spajanje, kupovinu ili stečaj, zamjenjuje u potpunosti ili djelimično novi pravni sljedbenik, odnosno privredni subjekat, koji ispunjava prvobitno određene uslove zaključenog ugovora o javnoj nabavci, a izmjene su predviđene tenderskom dokumentacijom, pod uslovom da se ne vrše druge bitne izmjene ugovora iz člana 150 stav 2 ZJN.

14. ZAHTJEV ZA POJAŠNJENJE ILI IZMJENU I DOPUNU TENDERSKE DOKUMENTACIJE

Privredni subjekat može da predloži naručiocu da izmijeni i/ili dopuni tendersku dokumentaciju, u roku od osam dana od dana objavljivanja, odnosno dostavljanja tenderske dokumentacije u skladu sa članom 94 st. 4 i 5 Zakona o javnim nabavkama. 

Privredni subjekat ima pravo da pisanim zahtjevom traži od naručioca pojašnjenje tenderske dokumentacije najkasnije deset dana prije isteka roka određenog za dostavljanje ponuda.

Zahtjev se podnosi isključivo putem ESJN-a.
15 IZJAVA NARUČIOCA O NEPOSTOJANJU SUKOBA INTERESA

[image: image3.emf]
15. UPUTSTVO O PRAVNOM SREDSTVU
Privredni subjekat može da izjavi žalbu protiv ove tenderske dokumentacije Komisiji za zaštitu prava:

   1) u roku od 20 dana od dana objavljivanja, odnosno dostavljanja tenderske dokumentacije ili izmjene i dopune tenderske dokumentacije, ako je rok za podnošenje prijava za kvalifikaciju, odnosno ponuda najmanje 30 dana od dana objavljivanja, odnosno dostavljanja tenderske dokumentacije ili izmjene i dopune tenderske dokumentacije;

   2) u roku od deset dana od dana objavljivanja, odnosno dostavljanja tenderske dokumentacije ili izmjene i dopune tenderske dokumentacije, ako je rok za podnošenje prijava za kvalifikaciju, odnosno ponuda najmanje 15 dana od dana objavljivanja, odnosno dostavljanja tenderske dokumentacije ili izmjene i dopune tenderske dokumentacije;

   3) do isteka polovine roka za podnošenje prijava za kvalifikaciju, odnosno ponuda, ako je rok za podnošenje prijava za kvalifikaciju, odnosno ponuda kraći od 15 dana od dana objavljivanja, odnosno dostavljanja tenderske dokumentacije ili izmjene i dopune tenderske dokumentacije, a u slučaju da je posljednji dan roka za podnošenje ponuda kraći od 24 časa, smatra se da rok ističe istekom tog dana.

Žalba se izjavljuje preko naručioca neposredno putem ESJN-a. Žalba koja nije podnesena na naprijed predviđeni način biće odbijena kao nedozvoljena. Podnosilac žalbe je dužan da uz žalbu priloži dokaz o uplati naknade za vođenje postupka u iznosu od 1% od procijenjene vrijednosti javne nabavke, a najviše 20.000,00 eura, na žiro račun Komisije za zaštitu prava broj 530-20240-15 kod NLB Montenegro banke A.D. Ukoliko je predmet nabavke podijeljen po partijama, a žalba se odnosi samo na određenu/e partiju/e, naknada se plaća u iznosu 1% od procijenjene vrijednosti javne nabavke te/tih partije/a.Instrukcije za plaćanje naknade za vođenje postupka od strane žalilaca iz inostranstva nalaze se na internet stranici Komisije za zaštitu prava nabavki http://www.kontrola-nabavki.me/.“.
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TEHNICKA DOKUMENTACIJA

Za projekat spoljne rasvjete u VN postrojenju

TS 400/110 kV — PODGORICA 2

OPIS RADOVA: Zamjena postojeceg sistema spoljasnje rasvjete VN postrojenja
OBJEKAT: Trafostanica 400/110 kV, Podgorica 2
LOKACUJA: Partizanski put bb, Podgorica, Crna Gora

INVESTITOR: Crnogorski elektroprenosni sistem AD, Podgorica

1. PREDMET PROJEKTA:

Za potrebe Investitora (CGES-a), potrebno je izvrsSiti zamjenu dotrajalih svetiljki postoje¢eg sistema
osvetljenja spoljne rasvjete (SR) trafostanice, sa novijim energetski efikasnijim LED svetiljkama, uz
obezbjedivanje boljih uslova osvijetljenosti u odnosu na postojece stanje. Obzirom na dotrajalost i stanje
postojecih instalacija, predvida se kompletna zamjena svih djelova sistema spoljne rasvjete novim. To
obuhvata demontazu svih postojecih, zatim nabavku, transport i ugradnju novih elemenata tj. svjetiljki,
pod-konstrukciju za iste, kablova za napajanje ormana i svjetiljki kao i ormane za razvod i upravljanje
rasvjetom.

2. CILJ PROJEKTA:

Rekonstrukcijom postojeéeg sistema spoljasnje rasvjete planirano je unapredenje osvijetljenosti VN
postrojenja u cilju zadovoljenja standarda, povecanje energetske efikasnosti i smanjenje emisije CO2,
smanjenje troskova odrzavanja, kao i povecanje bezbjednosti kretanja i obavljanja radnih zadataka kroz
VN postrojenje u no¢nim satima.

3. LOKACIJA

Predmenta lokacija se nalazi na katastarskoj parceli br. 3443, KO. Tolosi, pozicionirana paralelno sa
ulicom Partizanski put bb, gdje je i saobracajni pristup. Lokacija je na ravnom terenu, pravilnog oblika
na kojoj se nalazi postrojenje 400 kV i 110 kV, komandna zgrada sa pomoénim objektima. Povrsina
parcele je » 44.000 m?,
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4. OPIS POSTOJECEG STANJA
4.1 Od GRO-a do RO-a tabela 1.
DOVODNI KABAL (POLJE HV 7 (0.4 kv) - RAZVODNI ORMAR NA STUB (RO)

STUB/KABAL OZNAKA KABLA TIP KABLA OZNAKA KABLA TIP KABLA
STUB A STUB A PP41-Y 8x2.5 mm? STUB A PP41-Y 2x10 mm?
STUB B STUB B PP41-Y 8x2.5 mm? STUB B PP41-Y 3x10 mm?
STUB C STUB C-A PP41-Y 8x2.5 mm? STUB C-B PP41-Y 8x2.5 mm?
STUB D STUB D PP41-Y 8x2.5 mm? STUB D PP41-Y 4x6 mm?
STUB E STUB E PP41-Y 8x2.5 mm? STUBE PP41-Y 2x10 mm?

Tabela 1.
4.2. Od GRO-a do RO-a tabela 2.

ODVODNI KABAL (RAZVODNI ORMAR NA STUB (RO)) — RAZVODNA KUTIJA (VRH STUBA)

STUB/KABAL TIP KABLA
STUB A-E PP0OO-Y 2 x 5x2.5 mm?

Tabela 2.

4.3. RAZVODNI ORMARI

RAZVODNI ORMAR NA STUB (RO) (Slika 1. i Slika 2.)

Slika 1. Slika 2.

4.4, MONTAZNI STUBOVI ZA RASVJETU (Slika 3., Slika 4., Slika 5. i Slika 6.)

Stubovi su izradeni od Zeljezno-resetkaste konstrukcije visine 25 m, sa platformom za bezbjedan
pristup svetiljkama. Zastitni rukohvat je u obliku pravilnog osmougla izradenog od profila UNP 65
duzine po 85cm.
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Slika 3. Slika 4.

Slika 5. Slika 6.

5. PROJEKTOVANI RADOVI

5.1 RASVJETA | PRORACUN

Projektom je predvidena zamjena postojecih svetiljki sa novim LED svjetiljkama koje posjeduju dodatnu
zaStitu od prenapona, u broju i pozicijama potrebnim za zadovoljenje nivoa osvjetljaja prema standardu
MEST EN 12464-2:2014. Po ovom standardu, u tabeli 5.11 za elektrane | postrojenja, za “Overall
Inspection” zahtjeva se srednji osvjetljaj od 50Ix | ravnomjernost 0.4. Ovaj standard je potrebno
zadovoljiti u zonama razvodnih postrojenja (RP) 110 i 400kV, kao i energetskih transformatora (ETR).
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Pored gore popisanih postrojenja, na predmetnoj lokaciji postoje jo$ nekoliko razli¢itih zona/prostora
koje je potrebno osvijetliti u sledeé¢im nivoima osvijetljenosti i ravnomjernosti:

- Ulazna kapija - srednja osvijetljenost >30Ix / ravhomjernost >0.4.

- Ulazni koridor — srednja osvijetljenost >20Ix / ravnomjernost >0.4.

- Ostali koridori i staze — srednja osvijetljenost >20Ix / ravnomjernost >0.2.

- Perimetri (zone uz ograde) — srednja osvijetljenost >10Ix / ravhomjernost >0.2.

Osim zamjene svetiljki projekat obuhvata i promjenu nacina regulacije i upravljanja svetiljki sa ciljem
racionalizacije potrosnje elektricne energije kao i samog intervala rada svetiljki (u dva nivoa — dva
paljenja tj. dvije zone). Zona 1, definiSe opsti nivo za cirkulaciju postrojenjem, dok zona 2 definise
maksimalni nivo, kojim se ispunjava gore opisani standard. U osnovnom rezimu, tj. zoni 1 rasvjete,
potrebni nivoi osvijetljenosti i ravnomjernosti su:

- Ulazna kapija — srednja osvijetljenost >20Ix / ravhomjernost >0.4.

- Ulazni koridor — srednja osvijetljenost >10Ix / ravnomjernost >0.4.

- Postrojenja — srednja osvijetljenost >20Ix / ravhomjernost >0.2.

- ETR - srednja osvijetljenost >15Ix / ravhomjernost >0.4.

- Ostali koridori i staze — srednja osvijetljenost >10Ix / ravnomjernost >0.2.

- Perimetri (zone uz ograde) — srednja osvijetljenost >5Ix / ravnomjernost >0.2.

Fotometrijskim proracunom je potrebno zadovoljiti trazene vrijednosti za obije zone upravljanja
rasvjetom, te iste prikazati kao posebne scene u proracunu. Prilikom izvodenja, izvodac treba da postuje
sve pozitivne zakonske propise i prakse i da u skladu sa istima vrsi radove, bez obzira da li su isti navedeni
ili nisu u ovom projektu. Na podlogama za fotometrijski proracun dati su kompletni detalji potrebni za
izradu proracuna, sa svim ucrtanim elementima, njihovim dimenzijama i uputima za njihovo formiranje
u samom proracunu. Elemente date na podlozi je obavezno tretirati u proracunu.

U cilju provjere ispravnosti fotometrijskog proracuna, Izvodac je duzan dostaviti fotometrijski fajl (.evo
npr) kako bi Investitor mogao provjeriti sve elemente proracuna.

5.2 KABLOVSKA INSTALACIJA | RAZVODNI ORMANI

Projektom je previdena komplet zamjena napojnih kablova, na relaciji od ormana HV1 (odakle se napaja
sistem spoljne rasvjete) do ormana GOSR (glavni orman spoljne rasvjete), zatim svi kablovi na relaciji od
GOSR do lokalnih ormana na stubovima rasvjete i lokalnih svjetiljki na fasadi objekta.

GOSR je predviden kao nadgradni, na zidu u ulaznoj prostoriji dijela zgrade u kom se nalazi NN razvod.
Za isti je predvideno napajanje sa postojeCeg ormana HV1, gdje je potrebno izraditi prikljucak sa
postojecih sabirnica ormana. U istom je potrebno smijestiti i prekidacku/osiguracku opremu ,driser” za
zastiti glavnog napojnog kabla ka GOSR. Napojni kabl do GOSR je tipa NYCY 4x25mm2, kojeg stite
nozasti osigura¢ NHO1C 63A. Kabl se polaze kroz postojeée betonske kablovske kanale, a dio od
kablovskog kanala do ormana GOSR po zidu se polaze u PNK regalu 200mm.

Sa GOSR se napajaju svi lokalni ormani po stubovima rasvjete, kablovima tipa NYCY 4x10mm2. Kablovi
se polazu kroz postojece betonske kanale i cijevi, do krajnjih tacaka postojecih kanala blizu stubova,
zatim dijelom u zemljanom rovu do samih stubova, gdje se polazu nadgradno u PNK regalima 50mm

Bulevar Svetog Petra Cetinjskog 18, 81000 Podgorica, Crna Gora, www.cges.me,
Ziro racun: 510-27152-64, PIB: 02751372, PDV: 30/31-08699-3





ELEKTROPRENOS

((TS CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

po betonskom temelju i uz stub do pripadajuc¢ih ormana. Sa GOSR se jo$ napajaju svjetiljke i foto-celija
na fasadi objekta, kablovima tipa NYCY 3x1.5mm2. Ovi kablovi se dijelom polazu kroz postojece
betonske kanale i cijevi, do ulaska u objekat, zatim unutrasnjim zidovima objekta u PVC kanalicama do
pozicije svjetiljki.

Sa lokalnih ormana stubova rasvjete (RO A, B, C, D i E) se napajaju svjetiljke na stubovima, kablovima
tipa NYCY 3x2.5mma2. Kablovi se od pripadaju¢eg RO vodi do svake svjetiljke, nadgradno po metalnoj
konstrukciji stuba, pricvrscujuéi se na svakih 1m za istu. Za napajanje svjetiljki na dijelu portala u
RP110kV, polaze se kabl NYCY 5x2.5mm2, koji se dijelom polaze u iskopane rovove u zemlji, dijelom u
postojece betonske kablovske kanale, a dijelom nadgradno uz celi¢nu konstrukciju stubova portala do
pozicije svjetiljki.

Komanda (paljenje) rasvjete je predvideno putem dva grebenasta prekidaca koji ¢e biti montirani na
malom ormanu KO u komandnoj sobi komandne zgrade. Zona 1 kao osnovni scenario ¢e se paliti preko
preklopke ,1-0-2" koja omogucava ru¢no paljenje (polozaj 1) i automatski rad preko foto-Celije (polozaj
2). Zona 2 kao maksimalni scenario ce se paliti pomocu preklopke ,1-0". U tu svrhu od GOSR do pozicije
ormana KO se polaze kabl tipa NYCY 5x1.5mm2. Ovaj kabl se dijelom polaze kroz postojece betonske
kanale i cijevi, do ulaska u objekat, zatim unutrasnjim zidovima objekta u PVC kanalicama, zatim duplim
podom do pozicije KO u komandnoj sobi.

Ormani na stubovima rasvjete (RO-A,... RO-E) moraju biti nadgradni, predvideni za montazu na metalnu
konstrukciju stubova. Ormani moraju biti izradeni od poliestera ojacanog staklenim vlaknima otporan
na UV zracenja i atmosferske uticaje, u zastiti IP55.

Zbog blizine transformatora i relativno kratkih dionica kablova u energetskom smislu, sva sklopna
tehnika koriStena u ormanima mora biti isklopne modi 15kA.

5.3 POD-KONSTRUKCIA | MONTAZNO/DEMONTAZNI RADOVI

Ovim projektom se ne tretiraju postojeéi montazni stubovi za rasvjetu, vec se oni zadrzavaju. Na njima
se demontiraju postojece svjetiljke i predvida montaza novih. Prilikom radova demontiraju se svi ormani,
kablovi i pod-konstrukcija koja se nalazi na njima a nije funkcionalni dio stuba. Za nove svjetiljke bilo
one na stubovima rasvjete ili portalima u RP110kV, da bi zadovoljile potrebne uglove orijentacije (po X
i'Y osi) kao i inklinaciju (po Z osi), potrebno je izraditi dodatnu pod-konstrukciju kako se iste uklopile na
postojecu konstrukciju stubova rasvjete. Tacan nacin uklapanja definisati na licu mjesta, u zavisnosti od
usvojenog fotometrijskog rjeSenja. Pod-konstrukcija (nosac) mora imati gumenu barijeru na mjestu
montaze svjetiljke radi galvanskog odvajanja same svjetiljke od metalne mase stuba.

Uz demontazu svih nepotrebnih metalnih elemenata postoje¢e podkonstrukcije, potrebno je
demontirati sve ormane, svjetilike i kablove tretirane ovim projektom. Svu demontiranu opremu
skladistiti u magacinu Investitora.

5.4 ZAVRSNE ODREDBE
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Nakon svih izvedenih radova, Izvodac je duzan da izvrsi testiranje i pustanje u rad spoljne rasvjete u
prisustvu predstavnika Investitora. Po pustanju u rad, neophodno je izvrsiti mjerenje nivoa osvjetljaja u
skladu sa tackama iz fotometrijskog proracuna. Devijacije u odnosu na proracunske vrijednosti ne smiju
biti vece od 10%.

6. PRILOZI

6.1 NUMERICKA DOKUMENTACIA

Bilans snaga i energije — Spoljna rasvjeta TS PG 2
Proracun napojnih kablova — Spoljna rasvjeta TS PG 2
Fotometrijski prorac¢un: Rasvjeta outoodr pogona TS PG 2

6.2 GRAFICKA DOKUMENTACIA

Prilog 1 — Situacija: Glavni razvod napojnih kablova SR R =1:500
Prilog 2 — Razvod rasvjete na stubu A R=1:100
Prilog 3 — Razvod rasvjete na stubu B R=1:100
Prilog 4 — Razvod rasvjete na stubu C R=1:100
Prilog 5 — Razvod rasvjete na stubu D R=1:100
Prilog 6 — Razvod rasvjete na stubu E R=1:100
Prilog 7 — Situacija: dio RP 110kV : Razvod kablova SR R=1:200
Prilog 8 — Situacija: komandna zgrada : Razvod kablova SR R=1:200

Prilog 9 — Jednopolna Sema ormana GOSR

Prilog 10 — Jednopolna Sema ormana RO-A

Prilog 11 — Jednopolna Sema ormana RO-B

Prilog 12 — Jednopolna Sema ormana RO-C

Prilog 13 — Jednopolna $ema ormana RO-D

Prilog 14 — Jednopolna $ema ormana RO-E

Prilog 15 — Jednopolna Sema ormana KO

Prilog 16 — Blok Sema napajanja SR

Prilog 17 — Legenda opreme

Prilog 18 — Situacija: Podloga za fotometrijski proracun R =1:500
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BILANS SNAGA

. . . i s Instal. Snaga | Koef. Jedn. snaga
Tip potrosaca Razvodni orman - Potrosac (W) jednovr. (W)
RO - A 2,104 1.00 2,104
RO-B 2,104 1.00 2,104
RO-C 3,744 1.00 3,744
GOSR
RO-D 4,054 1.00 4,054
RO-E 3,419 1.00 3,419
FASADA 152 1.00 152
Ukupna instalisana snaga (W) 15,577
Koeficijent jednovremenosti (K) 1.00
Ukupna jednovremena snaga (W) 15,577
Ukupna aktivha snaga P (W) 15,577
Cos ¢ 0.95
Ukupna prividna snaga S (VA) 16,397
Potrebna godisnja energija (kWh) | 34,114
Podgorica, Oktobar 2024. Pripremio:

Blazo Jankovié, dipl. ing. el.






TABELA 1.

PRORACUN NAPOJNIH KABLOVA

o | oo TR0 T e [ s | o iresicana[ oo ] S [ o [er[o] =
od do P; (W) ki Pi(W)|cosg| I,(A) (mm?) l4(A) Il Ko | Ko | Ki | L(A) 1A /| 12(A) |1,45x, / I(m) % %
HV1 GOSR 15,577 1.00 15,577 0.95 | 23.69 NYCY 4x25 95 C [0.80(1.00|1.00( 76.00 [ 63 [1.60| 100.80 | 110.20 | zadov. 20 0.139 | 0.139

GOSR RO-A 2,104 1.00 2,104 0.95 3.20 NYCY 4x10 54 C [0.80(0.80|1.00( 34.56 | 32 (1.35| 43.20 | 50.11 | zadov. | 311 0.730 | 0.869
GOSR RO-B 2,104 1.00 2,104 0.95 3.20 NYCY 4x10 54 C [0.80(0.80(1.00| 34.56 | 32 (1.35( 43.20 | 50.11 | zadov. | 163 0.383 | 0.522
GOSR RO-C 3,744 1.00 3,744 0.95 5.70 NYCY 4x10 54 C [0.80(0.80|1.00( 34.56 | 32 [1.35| 43.20 | 50.11 | zadov. | 267 1.116 1.255
GOSR RO-D 4,054 1.00 4,054 0.95 6.17 NYCY 4x10 54 C [0.80(0.80(1.00( 34.56 | 32 [1.35| 43.20 | 50.11 | zadov. | 161 0.728 | 0.868
GOSR RO-E 3,419 1.00 3,419 0.95 5.20 NYCY 4x10 54 C [0.80(0.80|1.00( 34.56 | 32 [1.35| 43.20 | 50.11 | zadov. | 259 1.533 1.672
RO-C Cc2 468 1.00 468 0.95 214 NYCY 3x2.5 30 E 10.80/0.80|1.00| 19.20 | 16 |1.35| 21.60 | 27.84 | zadov. 25 0.316 1.571

"A" - tip elektri¢nog razvoda: prema JUS N.B2. 752 1T <I,<l

"B" - trajno dozvoljena struja 1,=In x K, x Kg x Ky (A) 2.1, <1.45x,

"C" - I, - nazivna struja zastitnog uredjaja - osiguraca (A). K, - zbog paralelnog vodjenja kablova

"D" - koeficijent zastitnog uredjaja - osiguraca (k) Kpg - zbog temperature ambijenta

"E" - I, = I,k - struja kod koje zastitni uredaj pouzdano djeluje (A) K, - zbog termi¢ke otpornosti zemlje

Pripremio:

Podgorica, Oktobar 2024.

Blazo Jankovi¢, dipl. ing. el.
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Description
RASVJETA OUTDOOR POGONA - TS PODGORICA 2 Glavni inZenjer u Sluzbi eksplo.

Blazo Jankovi¢

CGES AD Podgorica
Bul.Sv. Petra Cetinjskog 18

T+38269 010553
F+38220416 836
blazo.jankovic@cges.me

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 4
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The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 5
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The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 6
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Drotal Ptotal Luminous efficacy
2088250 Im 15577.0 W 134.17 Im/W
pcs. Manufacturer Article No. Article name P P Luminous efficacy
3 LUG Light 120202.5L POWERLUG LED ED 23950lm/740 IP65 50st. szary 155.0W 23950 Im 154.5 Im/W
Factory 091.22 easy connect
7 LUG Light 120202.5L POWERLUG LED ED 23250lm/740 IP65 as szeroki 155.0W 23250 Im 150.0 Im/W
Factory 091.42 szary easy connect
4 LUG Light 120202.5L POWERLUG LED ED 11950lm/740 IP65 as szeroki 77.0W 11950 Im  155.2 Im/W
Factory 121.41 szary
3 LUG Light 120212.5L POWERLUG MINI LED ED 3600Im/740 IP65 as 250w 3600 Im  144.0 Im/W
Factory 171.41 szeroki szary
29 LUG Light 120220.5L PUMA ED 61500Im/740 IP66 35st. 4680W  61500Im 131.4 Im/W
Factory 010.003
3 LUG Light 130222.5L  URBINO LED ED 3850im/740 IP66 091 szary I klasa  24.0W 3850 Im  160.4 Im/W
Factory 681.671

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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Product data sheet

LUG Light Factory - POWERLUG LED ED 11950Im/740 IP65 as szeroki szary

105° 105°
® 90° 90°
75° 750
60° 60°
Article No. 120202.5L121.41 s
45° 45°
P 77.0W
400
¢’Lamp 11950 Im
500
DLuminaire 11950 Im
30° 15° 0° 15° 30°
n 10000 % cd/kln(‘:O»CwO = C90 - C270 N=00%
Luminous efficacy 155.2 Im/W Polar LDC
CCT 4000 K
CRI 70

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 8
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Product data sheet

LUG Light Factory - POWERLUG LED ED 23250Im/740 IP65 as szeroki szary easy connect

105° 105°
® 90° 20°
75° 750
60° 800
Article No. 120202.5L091.42 s
45° o
P 155.0 W
400
¢’Lamp 23250 Im
500
PLuminaire 23250 Im
30° 15° 0 15° 30°
i 10000% Cd/klnémmso ——C90-C270 n=100%
Luminous efficacy 150.0 Im/W Polar LDC
CCT 4000 K
CRI 70

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 9
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Product data sheet

LUG Light Factory - POWERLUG LED ED 23950Im/740 IP65 50st. szary easy connect
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105°

90°

75°

60°

45°

1200

105°

90°

75°

60°

45°

Article No. 120202.5L091.22
P 155.0 W

®ramp 23950 Im
®Luminaire 23950 Im

n 100.00 %
Luminous efficacy 154.5 Im/W

CCT 4000 K

CRI 70

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.

30° 15° 0° 15° 30°
cd/kim n=100%
C0-C180 == C90-C270
Polar LDC
10
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Product data sheet

LUG Light Factory - POWERLUG MINI LED ED 3600Im/740 IP65 as szeroki szary

105° 105°
® 90° 90°
75° 750
60° 50°
300
Article No. 120212.5L171.41
P 50w 45° 400 45°
500
¢’Lamp 3600 Im
600
(DLuminaire 3600 |m
30° 15° 0 15° 30°
n 100.00 % cd/kln(]:mmso ——C90-C270 oo
Luminous efficacy 144.0 Im/W Polar LDC
CCT 4000 K
CRI 70

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 11
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Product data sheet

LUG Light Factory - PUMA ED 61500Im/740 IP66 35st.

LUG

Article No. 120220.5L010.003
P 468.0 W

®ramp 61500 Im
®Luminaire 61500 Im

n 100.00 %
Luminous efficacy 131.4 Im/W

CCT 4000 K

CRI 70
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105° 105°

90° 90°

75° 75°
800

60° 60°
1200

45° 1600 45°
2400

30° 15° 0° 15° 30°

cd/klm n=100%

C0-C180 =—=C90-C270

Polar LDC

E(0°) 502843
E(C90) 17.3° 219978

0.50 E(CO)  17.4° 218701
E(0%) 125711

E(C90) 17.3° 54994

1.0 E(CO) 17.4° 54675
E(0°) 55871

E(CO0) 17.3° 24442

15 E(CO) 17.4° 24300
E(0°) 31428

E(C90) 17.3° 13749

20 E(CO) 17.4° 13669
E(0°) 20114

E(C90) 17.3° 8799

25 E(CO) 17.4° 8748
E(0°) 13968

: E(C90) 17.3° 6110

3.0 1.9 E(CO) 17.4° 6075
Distance [m] Cone diameter [m] Illluminance [Ix]

= C0 - C180 (Beam angle: 34.8°)
=== C90 - C270 (Beam angle: 34.6°)

Cone diagram

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.
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Product data sheet
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LUG Light Factory - URBINO LED ED 3850Im/740 IP66 O91 szary I klasa

LUG

105°

90°

75°

60°

450

45°

600

750

105°

90°

45°

Article No. 130222.5L681.671
P 240W

®ramp 3850 Im

®ruminaire 3850 Im

n 100.00 %
Luminous efficacy 160.4 Im/W

CCT 4000 K

CRI 70

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.

30° 15° 0° 15° 30°
cd/kim n=100%
C0-C180 == C90-C270
Polar LDC
13
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Site 1
Luminaire layout plan
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The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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Site 1

Luminaire layout plan
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LUG Light Factory - 120202.5L091.22 - POWERLUG LED ED 23950Im/740 IP65 50st. szary easy

connect

1x LED 4000K

X Y Mounting height Housing rotation MF Luminaire
89.152 m 141.611m 25.000 m -0.0°/-35.0°/110.0° 0.90
89.152m 138.994 m 25.000 m 0.0°/-35.0°/-105.0° 0.90
166.119 m 113.264 m 25.800 m 0.0°/-25.0°/-65.0° 0.90

LUG Light Factory - 120202.5L091.42 - POWERLUG LED ED 23250Im/740 IP65 as szeroki szary easy

connect

1x LED 4000K

X Y Mounting height Housing rotation MF Luminaire
155.015m 257.561m 25.000 m -0.0°/-10.0°/-135.0° 0.90
25250 m 154.522 m 9.500 m 0.0°/-20.0°/-0.0° 0.90
25.250 m 136.522 m 9.500 m 0.0°/-20.0°/-0.0° 0.90
25250 m 118,519 m 9.500 m 0.0°/-25.0°/-0.0° 0.90
25.250 m 100.522 m 9.500 m 0.0°/-25.0°/-0.0° 0.90
25250 m 82.520m 9.500 m 0.0°/-20.0°/-0.0° 0.90
25.250 m 64.523 m 9.500 m 0.0°/-20.0°/-0.0° 0.90

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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Site 1

Luminaire layout plan
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LUG Light Factory - 120202.5L121.41 - POWERLUG LED ED 11950Im/740 IP65 as szeroki szary
1x LED 4000K

X Y Mounting height Housing rotation MF Luminaire
157.005m 259.460 m 25.000 m 0.0°/-0.0°/35.0° 0.90
167.387 m 114.748 m 25.800 m 0.0°/-0.0°/-0.0° 0.90
119.694 m 74989 m 8.000 m 0.0°/-20.0°/90.0° 0.90
18.705m 18317 m 25.000 m -0.0°/5.0°/-135.0° 0.90

LUG Light Factory - 120212.5L171.41 - POWERLUG MINI LED ED 3600Im/740 IP65 as szeroki szary
1x LED 4000K

X Y Mounting height Housing rotation MF Luminaire
77.869 m 81.255m 5.000 m 0.0°/-15.0°/-180.0° 0.90
97.800 m 74.950 m 5.000 m -0.0°/-20.0°/90.0° 0.90
77.869 m 62.664 m 5.000 m 0.0°/-15.0°/-180.0° 0.90

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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Luminaire layout plan
LUG Light Factory - 120220.5L010.003 - PUMA ED 61500Im/740 IP66 35st.
1x LED 4000K
X Y Mounting height Housing rotation MF Luminaire
154.664 m 258.470 m 25.000 m 60.0°/-0.0°/90.0° 0.90
155.091T m 257.653 m 25.800 m 60.0°/-0.0°/140.0° 0.90
155.927 m 257.244 m 25.000 m 65.0°/-0.0°/175.0° 0.90
155919 m 257.236 m 25.800 m 65.0°/-0.0°/160.0° 0.90 IEI
65.899 m 217.767 m 25.800 m 65.0°/0.0°/-45.0° 0.90
64.902 m 217.401 m 25.800 m 65.0°/-0.0°/45.0° 0.90
66.790 m 217.345m 25.800 m 60.0°/-0.0°/-65.0° 0.90 IEI
64.576 m 216.484 m 25.800 m 65.0°/-0.0°/125.0° 0.90
67.097 m 216.464 m 25.800 m 55.0°/0.0°/-90.0° 0.90
64911 m 215614 m 25.800 m 65.0°/0.0°/160.0° 0.90
66.763 m 215.602 m 25.800 m 60.0°/0.0°/-130.0° 0.90
65.744 m 215239 m 25.800 m 65.0°/0.0°/170.0° 0.90
89.152 m 141.408 m 25.800 m -55.0°/0.0°/160.0° 0.90
90.129 m 141.224 m 25.800 m -65.0°/0.0°/125.0° 0.90
88.220m 141178 m 25.800 m -60.0°/0.0°/-115.0° 0.90
87.821m 140.320m 25.800 m -60.0°/0.0°/-55.0° 0.90
90.321m 140.284 m 25.800 m -65.0°/0.0°/110.0° 0.90
88.275m 139.476 m 25.000 m -65.0°/0.0°/-45.0° 0.90
88.214 m 139.458 m 25.800 m -65.0°/0.0°/-35.0° 0.90
90.104 m 139.300 m 25.800 m 50.0°/-0.0°/-135.0° 0.90
165.945m 115.887 m 25.800 m 65.0°/-0.0°/15.0° 0.90

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 17
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Site 1
Luminaire layout plan
X Y Mounting height Housing rotation MF Luminaire
165.095 m 115.575m 25.800 m 65.0°/-0.0°/ 30.0° 0.90
164642m  114579m  25800m 65.0°/0.0°/ 40.0° 0.90
164.642 m 114579 m 25.000 m 55.0°/0.0° / 90.0° 0.90
19.755 m 20521 m 25.800 m 65.0°/-0.0°/-30.0° 0.90
19.755m 20.521 m 25.000 m 65.0° /-0.0° / -40.0° 0.90
20.687 m 20191 m 25.000 m 65.0°/-0.0°/ -55.0° 0.90
20687 m 20191 m 25800 m 65.0°/0.0°/ -45.0° 0.90
20,985 m 19.248'm 25.800 m 65.0°/0.0° / -85.0° 0.90

LUG Light Factory - 130222.5L681.671 - URBINO LED ED 3850Im/740 IP66 O91 szary [ klasa
1x LED 4000K

X Y Mounting height Housing rotation MF Luminaire
22903 m 154.522 m 9.000 m 15.0°/0.0°/90.0° 0.90
22903 m 118.522 m 9.000 m 15.0°/0.0°/90.0° 0.90
22903 m 64.522 m 9.000 m 15.0°/0.0°/90.0° 0.90

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 18
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Site 1 (Light scene 1 - Nivo 1 (FULL))
Calculation objects

DV
Va0,
Viag
STy,
A

©
<3

A 0L APNIrOYLSOd

TEw www

(AN

>
2
m
<
z
A

.

(&

>
0.10 0.20 0.30 0.50 0.75 1.00 1.25 1.58 1.99 2.51 3.16 3.98 5.01 6.30 7.94
16 20 25 32 40 50 63 79 100 15000 [Ix]

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2 (G

Site 1 (Light scene 1 - Nivo 1 (FULL))
Calculation objects

Calculation surfaces

Properties E Emin Emax Us (g1) 92 Index
CS 1 - Ulazni koridor 27.21x 131 Ix 134 Ix 0.48 0.098
Perpendicular illuminance

Height: -0.000 m

CS 2 - Koridor 400kV 46.4 Ix 149 Ix 74.8 Ix 032 0.20
Perpendicular illuminance

Height: -0.000 m

CS 3 - Koridor 110kV 474 1x 10.7 Ix 131 Ix 0.23 0.082
Perpendicular illuminance

Height: 0.020 m

CS 4 - Centralni koridor 39.2 Ix 8.15 Ix 130 Ix 0.21 0.063
Perpendicular illuminance

Height: -0.000 m

CS5-RP110-1 60.9 Ix 26.5 Ix 102 Ix 0.44 0.26 CG5
Perpendicular illuminance

Height: 0.020 m

CS6-RP110-2 58.9 Ix 30.7 Ix 163 Ix 0.52 0.19 CG6
Perpendicular illuminance

Height: 0.020 m

CS 7 -RP 400 - 1 55.3 Ix 23.11x 150 Ix 0.42 0.15
Perpendicular illuminance

Height: 0.020 m

CS 8 -RP 400 -2 535 Ix 22.7Ix 173 Ix 0.42 0.13
Perpendicular illuminance

Height: 0.020 m

CS9-ETR-1 56.7 Ix 35.8Ix 100 Ix 0.63 0.36 CG9
Perpendicular illuminance

Height: -0.000 m

CS10-ETR-2 51.0 Ix 32.21x 140 Ix 0.63 0.23 CG10
Perpendicular illuminance

Height: -0.000 m

CS 11 - Perimetar 12.4 1x 3.07 Ix 98.3 Ix 0.25 0.031 CG11

Perpendicular illuminance
Height: 0.020 m

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 20
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Site 1 (Light scene 1 - Nivo 1 (FULL))
Calculation objects

CS 12 - Perimetar 15.6 Ix 7.13 1x 32.2 Ix 0.46 0.22 CG12
Perpendicular illuminance

Height: 0.020 m

CS 13 - Ulazna kapija 30.2 Ix 23.8 Ix 353 Ix 0.79 0.67 CG13
Perpendicular illuminance

Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 21
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Site 1 (Light scene 2 - Nivo 2 (LOW))
Calculation objects
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The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.
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SISTEM AD

10 12
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CRNOGORSKI
* ELEKTROPRENOSNI
SISTEM AD

RASVJETA OUTDOOR POGONA - TS PODGORICA 2 (G 4

Site 1 (Light scene 2 - Nivo 2 (LOW))
Calculation objects

Calculation surfaces

Properties E Emin Emax Us (g1) 92 Index
CS 1 - Ulazni koridor 13.9 Ix 6.53 Ix 30.6 Ix 0.47 0.21
Perpendicular illuminance

Height: -0.000 m

CS 2 - Koridor 400kV 22.6Ix 7.93 Ix 52.6 Ix 035 0.15
Perpendicular illuminance

Height: -0.000 m

CS 3 - Koridor 110kV 19.4 Ix 4.65 Ix 35.8 Ix 0.24 0.13
Perpendicular illuminance

Height: 0.020 m

CS 4 - Centralni koridor 16.1 Ix 3.62 Ix 107 Ix 0.22 0.034
Perpendicular illuminance

Height: -0.000 m

CS5-RP110-1 29.2 Ix 6.12 Ix 67.5 Ix 0.21 0.091 CG5
Perpendicular illuminance

Height: 0.020 m

CS6-RP110-2 23.1 Ix 10.6 Ix 118 Ix 0.46 0.090 CG6
Perpendicular illuminance

Height: 0.020 m

CS 7 -RP 400 - 1 27.11x 714 Ix 121 Ix 0.26 0.059
Perpendicular illuminance

Height: 0.020 m

CS 8 -RP 400 -2 20.9 Ix 6.53 Ix 122 Ix 0.31 0.054
Perpendicular illuminance

Height: 0.020 m

CS9-ETR-1 18.1 Ix 124 1x 52.7 Ix 0.69 0.24 CG9
Perpendicular illuminance

Height: -0.000 m

CS10-ETR-2 20.5Ix 9.84 Ix 107 Ix 0.48 0.092 CG10
Perpendicular illuminance

Height: -0.000 m

CS 11 - Perimetar 8.49 Ix 1.84 Ix 96.2 Ix 0.22 0.019 CG11

Perpendicular illuminance
Height: 0.020 m

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 23





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
Calculation objects

CS 12 - Perimetar 10.9 Ix 6.08 Ix 30.3 Ix 0.56 0.20 CG12
Perpendicular illuminance

Height: 0.020 m

CS 13 - Ulazna kapija 27.7 Ix 229 1Ix 32.01x 0.83 0.72 CG13
Perpendicular illuminance

Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 24





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 1 - Nivo 1 (FULL))
CS 1 - Ulazni koridor

./

[ | P I

12 16 20 25 32 40 50 63 79 100 15000 [Ix]

Properties E Emin Emax Uo (1) 92 Index
CS 1 - Ulazni koridor 27.2 I 13.1 Ix 134 Ix 0.48 0.098

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 25





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 1 - Nivo 1 (FULL))
CS 2 - Koridor 400kV

e o'd IF
A éa .
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M
12 16 20 25 32 40 50 63 79 [Ix]
Properties E Emin Emax Uo (1) 92 Index
CS 2 - Koridor 400kV 46.4 Ix 14.9 Ix 74.8 Ix 0.32 0.20

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 26





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 1 - Nivo 1 (FULL))
CS 3 - Koridor 110kV

| S e

10 12 16 20 25 32 40 50 63 79 100 15000 [Ix]

Properties E Emin Emax Uo (1) g2 Index
CS 3 - Koridor 110kV 47.4 1% 10.7 Ix 131 Ix 0.23 0.082

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 27





RASVJETA OUTDOOR POGONA - TS PODGORICA 2 (( S
'Ve CRNOGORSKI
ELEKTROPRENOSNI
=N SISTEM AD
Site 1 (Light scene 1 - Nivo 1 (FULL))
CS 4 - Centralni koridor
A
Y
O
<O
| . I ===
7.94 10 12 16 20 25 32 40 50 63 79 100 15000 [Ix]
Properties E Emin Emax Uo (1) 92 Index
CS 4 - Centralni koridor 39.2 Ix 8.15 Ix 130 Ix 0.21 0.063

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.

28





RASVJETA OUTDOOR POGONA - TS PODGORICA 2

((‘Veg CRNOGORSKI
ELEKTROPRENOSNI
=N SISTEM AD
Site 1 (Light scene 1 - Nivo 1 (FULL))
CS5-RP110-1

O
25 32 40 50 63 79 100 15000 [Ix]
Properties E Emin Emax Uo (1) 92 Index
CS5-RP110-1 60.9 Ix 26.5 Ix 102 Ix 0.44 0.26

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 1 - Nivo 1 (FULL))
CS6-RP110-2

2

”~

S e
25 32 40 50 63 79 100 15000 [Ix]
Properties E Emin Emax Uo (1) 92 Index
CS6-RP110-2 58.9 Ix 30.7 Ix 163 Ix 0.52 0.19

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 30





RASVJETA OUTDOOR POGONA - TS PODGORICA 2 (( S
'Ve CRNOGORSKI
ELEKTROPRENOSNI
— SISTEM AD
Site 1 (Light scene 1 - Nivo 1 (FULL))
CS7-RP400-1
o
O
)
S e
20 25 32 40 50 63 79 100 15000 [Ix]
Properties E Emin Emax Uo (1) 92 Index
CS7-RP400-1 55.3 Ix 23.1 Ix 150 Ix 0.42 0.15

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2 (( S
'Ve CRNOGORSKI
ELEKTROPRENOSNI
— SISTEM AD

Site 1 (Light scene 1 - Nivo 1 (FULL))

CS8-RP400-2

O
O
S e

20 25 32 40 50 63 79 100 15000 [Ix]

Properties E Emin Emax Uo (1) 92 Index
CS8-RP400-2 53.5 Ix 22.7 Ix 173 Ix 0.42 0.13

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2

C(‘VES CRNOGORSKI
ELEKTROPRENOSNI
N SISTEM AD

Site 1 (Light scene 1 - Nivo 1 (FULL))

CS9-ETR-1

32 40 50 63 79 100 15000 [Ix]

Properties E Emin Emax Uo (1) g2 Index
CS9-ETR-1 56.7 Ix 35.8 Ix 100 Ix 0.63 0.36

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.

33





RASVJETA OUTDOOR POGONA - TS PODGORICA 2

CCTGS CRNOGORSKI
ELEKTROPRENOSNI
=N SISTEM AD
Site 1 (Light scene 1 - Nivo 1 (FULL))
CS10-ETR-2

B I
32 40 50 63 79 100 15000 [Ix]
Properties E Emin Emax Uo (1) 02 Index
CS10-ETR-2 51.0 Ix 32.2 Ix 140 Ix 0.63 0.23 cG10

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 1 - Nivo 1 (FULL))
CS 11 - Perimetar

O - —
o
Q
J Il E=EEewoon -
2.51 316 398 501 630 794 10 12 16 20 25 32 40 50 63 79 100 [ix]
Properties E Emin Emax Uo (1) g2 Index
CS 11 - Perimetar 12.41x 3.07 Ix 98.3 Ix 0.25 0.031 CGM

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 35





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 1 - Nivo 1 (FULL))
CS 12 - Perimetar

O

6.30 7.94 10 12 16 20 25 32 40 [IX]
Properties E Emin Emax Uo (1) 92 Index
CS 12 - Perimetar 15.6 Ix 713 Ix 32.2 Ix 0.46 0.22 CG12

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 36





RASVJETA OUTDOOR POGONA - TS PODGORICA 2

((‘Vé CRNOGORSKI
ELEKTROPRENOSNI
=N SISTEM AD
Site 1 (Light scene 1 - Nivo 1 (FULL))
CS 13 - Ulazna kapija

3 7 5

33
2

3
20 25 32 40 [Ix]
Properties E Emin Emax Uo (a1) g2 Index
CS 13 - Ulazna kapija 30.2 Ix 23.8Ix 353 Ix 0.79 0.67

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS 1 - Ulazni koridor

6.30 7.94 10 12 16 20 25 32Ix]

Properties E Emin Emax Uo (1) 02 Index
CS 1 - Ulazni koridor 13.9Ix 6.53 Ix 30.6 Ix 0.47 0.21
Perpendicular illuminance

Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 38





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS 2 - Koridor 400kV

|| |

6.30 7.94 10 12 16 20 25 32 40 50 63 [Ix]

Properties E Emin Emax Uo (1) 92 Index
CS 2 - Koridor 400kV 22.6 Ix 7.93 Ix 52.6 Ix 0.35 0.15

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 39





RASVJETA OUTDOOR POGONA - TS PODGORICA 2 (( S
'VE CRNOGORSKI
ELEKTROPRENOSNI
=N SISTEM AD
Site 1 (Light scene 2 - Nivo 2 (LOW))
CS 3 - Koridor 110kV
|
]
|
|
. 4
|
[ || |
3.98 5.01 6.30 7.94 10 12 16 20 25 32 40 [IX]
Properties E Emin Emax Uo (1) 92 Index
CS 3 - Koridor 110kV 19.4 I 4.65 Ix 35.8 Ix 0.24 0.13

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS 4 - Centralni koridor

[ — | I ==

3.16 3.98 5.01 6.30 7.94 10 12 16 20 25 32 40 50 63 79 100 15000 [Ix]
Properties E Emin Emax Uo (1) 92 Index

CS 4 - Centralni koridor 16.1 Ix 3.62 Ix 107 Ix 0.22 0.034

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 41





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS5-RP110-1

"~
..

S IEE e P 0 0 0 0 ]

5.01 6.30 7.94 10 12 16 20 25 32 40 50 63 79 [IX]

Properties E Emin Emax Uo (1) 92 Index
CS5-RP110-1 29.2 Ix 6.12 Ix 67.5 Ix 0.21 0.091

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 42





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS6-RP110-2

"~
..

0
| B | I
10 12 16 20 25 32 40 50 63 79 100 15000 [Ix]
Properties E Emin Emax Uo (1) 92 Index
CS6-RP110-2 23.1 Ix 10.6 Ix 118 Ix 0.46 0.090

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 43





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS7-RP400-1

6.30 7.94 10 12 16 20 25 32 40 50 63 79 100 15000 [Ix]

Properties E Emin Emax Uo (1) 92 Index
CS7-RP400- 1 27.1 I 714 Ix 121 Ix 0.26 0.059
Perpendicular illuminance

Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 44





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS8-RP400-2

"~
..

Il . Y | I

6.30 7.94 10 12 16 20 25 32 40 50 63 79 100 15000 [Ix]

Properties E Emin Emax Uo (1) 02 Index
CS8-RP400-2 20.9 Ix 6.53 Ix 122 Ix 0.31 0.054
Perpendicular illuminance

Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed. 45





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS9-ETR-1

|

10 12 16 20 25 32 40 50 63 [Ix]

Properties E Emin Emax Uo (1) 02 Index
CS9-ETR-1 18.1 Ix 12.4 Ix 52.7 Ix 0.69 0.24

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 46





RASVJETA OUTDOOR POGONA - TS PODGORICA 2

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS10-ETR-2

(&

CRNOGORSKI
ELEKTROPRENOSNI
SISTEM AD

[ 20200 — |

7.94 10 12 16 20 25 32 40 50 63 79 100 15000 [1x]

Properties E Emin Emax Uo (1) 02 Index
CS10-ETR-2 20.51Ix 9.84 Ix 107 Ix 0.48 0.092

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/") CRNOGORSKI
ELEKTROPRENOSNI

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS 11 - Perimetar

SISTEM AD

‘,' —” TS |
I ... Il .. . e
1.58 1.99 2.51 3.16 3.98 5.01 6.30 7.94 10 12 16 20 25 32 40 50 63
79 100 [IX]
Properties E Emin Emax Uo (1) 92 Index
CS 11 - Perimetar 8.49 Ix 1.84 Ix 96.2 Ix 0.22 0.019 CG11

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2 (( S
'Ve CRNOGORSKI
ELEKTROPRENOSNI
=——\ SISTEMAD
Site 1 (Light scene 2 - Nivo 2 (LOW))
CS 12 - Perimetar
| |
5.01 6.30 7.94 10 12 16 20 25 32 [Ix]
Properties E Emin Emax Uo (1) 92 Index
CS 12 - Perimetar 10.9 Ix 6.08 Ix 30.3 Ix 0.56 0.20 CG12

Perpendicular illuminance
Height: 0.020 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2

Site 1 (Light scene 2 - Nivo 2 (LOW))
CS 13 - Ulazna kapija

(@

CRNOGORSKI
ELEKTROPRENOSNI
SISTEM AD

X,
20 25 32 40 [IX]
Properties E Emin Emax Uo (a1) g2 Index
CS 13 - Ulazna kapija 27.7 Ix 229 1Ix 32.01x 0.83 0.72 CG13

Perpendicular illuminance
Height: -0.000 m

Utilisation profile: Power, electricity, gas and heat plants (5.11.3 Overall inspection)

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary

depending on the conditions in which the luminaires are installed.
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RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1
Control group CG 1
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The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 51





RASVJETA OUTDOOR POGONA - TS PODGORICA 2
/) CRNOGORSKI
ELEKTROPRENOSNI

SISTEM AD

Site 1
Control group CG 2
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The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 52





RASVJETA OUTDOOR POGONA - TS PODGORICA 2 (G

CRNOGORSKI
ELEKTROPRENOSNI
SISTEM AD
Site 1
Control groups
Control group CG1 CG2
Light scene 1-Nivo 1 (FULL) 100 100
Light scene 2 - Nivo 2 (LOW) 100 -
Dimming values [%]
pcs. Manufacturer Article No. Article name P Index
3 LUG Light 120202.5L091.22 POWERLUG LED ED 23950Im/740 IP65 50st. szary easy 155.0 W
Factory connect
7 LUG Light 120202.5L091.42 POWERLUG LED ED 23250Im/740 IP65 as szeroki szary easy ~ 155.0 W
Factory connect
4 LUG Light 120202.5L121.41 POWERLUG LED ED 11950Im/740 IP65 as szeroki szary 77.0W
Factory
3 LUG Light 120212.5L171.41 POWERLUG MINI LED ED 3600Im/740 IP65 as szeroki szary 250W
Factory
29 LUG Light 120220.5L010.00 PUMA ED 61500Im/740 IP66 35st. 468.0 W
Factory 3
3 LUG Light 130222.5L681.67 URBINO LED ED 3850Im/740 IP66 091 szary I klasa 240W IEI
Factory 1

The project is not the offer as concerns law. The presented results are approximate and may change. The actual results may vary
depending on the conditions in which the luminaires are installed. 53





DV 400 kV TIRANA

A

DV 400 kV RIBAREVINE

PORTIRNICA

5 — D D D D u 5
Mu T f ! ! ! NYCY 4x10mm? (STUB B)
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\ NYCY 4x10mm? (STUB A)
I I I I
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e OVAJ CRTEZ JE U VLASNISTVU PREDUZECA CGES | NE SMIJE SE NI U SEGMENTIMA, NI U CJELOSTI
REPRODUKOVATI ILI KOPIRATI.
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STAZA

NYCY 3x1.5mm? (FASADA)

NYCY 3x1.5mm? +
NYCY 5x1.5mm?

NYCY 3x1.5mm? + NYCY 5x1.5mm?

S3/8.0m
Z1/F1

el

KOMANDNA ZGRADA

S2/5.0m

Z1/F1

NYCY 5x1.5mm? (na KO u komandnoj

sobi, za kontrolu rasvjete)

Svjetiljka tip S4

(54)/6m

NYCY 3x1.5mm?/(FASADA)

FC/2.5m
FoTo | Z1/21
|

GOSR -

NYCY 3x1.5mm? (Foto-celija)

NYCY 3x1.5mm? (FASADA)

NAPOMENA:

Visina montaze od kote zemlje

Broj strujnog kruga

Zona paljenja (Z1 - nizi nivo ; Z2 - viSi nivo)

e OVAJ CRTEZ JE U VLASNISTVU PREDUZECA CGES | NE SMIJE SE NI U SEGMENTIMA, NI U CJELOSTI
REPRODUKOVATI ILI KOPIRATI.

e SVE MJERE PROVJERITI NA LICU MJESTA, A SVAKO ODSTUPANJE OD PROJEKTA PRIJAVITI INVESTITORU.
DIMENZIJE SE NE SMIJU SKALIRATI/MIJENJATI.

B B
S2/5.0m S2/5.0m
Z1/F2 Z1/F2

STAZA
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(G -> CRNOGORSKI (G -> CRNOGORSKI
ELEKTROPRENOSNI ELEKTROPRENOSNI
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NYCY 5x1.5 mm?2
sa GOSR

NAPOMENE:

* - Grebenaste sklopke na vratima ormana, za komandu aktivnosti zona spoljne rasvjete (Z1 i Z22).
Natpis iznad sijalica "komanda Z1" i " komanda Z2".

** - Signalne sijalice 220V na vratima ormana, za signalizaciju dovodnih i odvodnih signala:

Z1D - Signalizacija dovoda signala Z1, zelene boje. Natpis "DOVOD Z1"

Z2D - Signalizacija dovoda signala Z2, zelene boje. Natpis "DOVOD Z2 "

Z1A - Signalizacija aktivacije signala Z1 - automatski rezim, crvene boje. Natpis " Z1 AUTO "

Z1R - Signalizacija aktivacije signala Z1 - ru¢ni rezim, crvene boje. Natpis " Z1 RUCNO "

Z20 - Signalizacija aktivacije signala Z2, crvene boje. Natpis " Z2 UKLJUCENO "
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———W SISTEM AD ———w SISTEM AD
Objekat: Trafostanica 400/110 kV, Podgorica 2 Lokacija: Kat. parcela broj 3443, KO Tolosi, Podgorica

Pripremio: Blazo Jankovi¢, d.i.e. Tehnicka dokumentacija: Razmijera:
Spoljna rasvjeta - TS PG 2 -1 -

Datum izrade: Prilog: Broj priloga: Br. strane:
Jednopolna Sema ormana KO 15 XX

10.2024. god.
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LEGENDA OPREME NA CRTEZIMA

koli¢ina

S1

Reflektorska svjetiljka 468W, uskog snopa optike 35°,
e 61500Im, CRI70, 4000K, IP66 1K08, 230Vac, sli¢na tipu
PUMA, LUG Poljska.

29

S2

Reflektorska svjetiljika 25W, Siroko-asimetri¢nog snopa
= optike ASW, 3600Ilm, CRI70, 4000K, IP65 IK09, 230Vac,
sli¢na tipu POWERLUG MINI, LUG Poljska.

S3

Reflektorska svjetilika 77W, Siroko-asimetrinog snopa
optike ASW, 11950Im, CRI70, 4000K, IP65 IK09, 230Vac,
sli¢na tipu POWERLUG, LUG Poljska.

S4

Ulicna svjetiljika 24W, Siroko-pojasnog snopa optike 091,
3850Im, CRI70, 4000K, 1P66, IK08, 230Vac, sli¢na tipu
URBINO, LUG Poljska.

S5

Reflektorska svjetilika 155W, Siroko-asimetricnog snopa
@ optike ASW, 23250Ilm, CRI70, 4000K, 1P65 IK09, 230Vac,
slicna tipu POWERLUG, LUG Poljska.

S6

Reflektorska svjetilika 155W, srednje-uskog snopa optike
50°, 23950Im, CRI70, 4000K, IP65, IK09, 230Vac, sli¢na tipu
POWERLUG, LUG Poljska.

FC

Foto-¢elija za paljenje/gasSenje SR . Vanjska montaza za
ugradnju na zid, minimalna zastita |P44.

4

Razvodni orman

LEGENDA OZNAKE SVJETILJKI

Svijetiljka tip S4 Visina montaze od kote zemlje

Broj strujnog kruga

Zona paljenja (Z1 - nizi nivo ; Z2 - viSi nivo)

NAPOMENA:

e OVAJ CRTEZ JE U VLASNISTVU PREDUZECA MONCORE DOO | NE SMIJE SE NI U SEGMENTIMA, NI U
CJELOSTI REPRODUKOVATI ILI KOPIRATI.

e SVE MJERE PROVJERITI NA LICU MJESTA, A SVAKO ODSTUPANJE OD PROJEKTA PRIJAVITI
PROJEKTANTU. DIMENZIJE SE NE SMIJU SKALIRATI/MIJENJATI.

LEGENDA OZNAKE ELEMENATA U TABLI GOSR
KZ1-A Kontaktor 2NO 40A - za paljenje zone 1 - Stub A
KZ2-A Kontaktor 1NO 40A - za paljenje zone 2 - Stub A
KZ1-B Kontaktor 2NO 40A - za paljenje zone 1 - Stub B
KZ2-B Kontaktor 1NO 40A - za paljenje zone 2 - Stub B
KzZ1-C Kontaktor 2NO 40A - za paljenje zone 1 - Stub C
Kz2-C Kontaktor 1NO 40A - za paljenje zone 2 - Stub C
KZ1-D Kontaktor 1NO 40A - za paljenje zone 1 - Stub D
KZ2-D Kontaktor 2NO 40A - za paljenje zone 2 - Stub D
KZ1-E Kontaktor 1NO 40A - za paljenje zone 1 - Stub E
KZ2-E Kontaktor 2NO 40A - za paljenje zone 2 - Stub E
KZ1-F Kontaktor 2NO 40A - za paljenje zone 1 - Fasada objekta
GS 1-0 Grebenasta sklopka/prekidac na vratima ormana
1-0, 1P, 20A, 230V
GS 1-0-2 Grebenasta sklopka/izbornik poloZaja na vratima
ormana 1-0-2, 1P, 20A, 230V
® Signalna sijalica 220V
FC Foto-¢elija na fasadi objekta.
S Upravljanje/kontrola zone 1
Upravljanje/kontrola zone 2
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166,81

262,21

NAPOMENE ZA PRIPREMU FOTOMETRIJSKIH PRORACUNA:

N

H=25m+0.8m ograda Sve kalkulacijske povrsine se postavljaju na 0.02m visine.

2. Svi objekti ucrtani na crtezu moraju biti tretirani i u proracunu, sa njihovim

R gp Lo visinama naznagenim na crtezu.

3. "Maintenance factor" svjetiliki moze biti maksimalno 0.9.

4. Mrezu kalkulacijskih tacaka na povrSinama prilagoditi tackama prikazanim na
crtezu.

5.  Za kalkulacijske povrsine perimetra i pjeSackih staza potrebno je imati isti broj
redova tacaka u oba smjera.

6. Za kalkulacijske povrSine u postrojenjima, maksimalna udaljenost tacaka
(grid) je 2x3m (gledano po uzoj strani).

7. Visine svjetiljki na stubovima u opsegu 25.0 - 25.8m (dno i vrh ograde). Iste je

potrebno predvidjeti sa nosatem i podkonstrukcijom za montazu na

stub/ogradu.

. Na portalima u 110kV postrojenju svjetiljike predvidjeti na maksimalno 9.5m.

9. Maksimalna inklinacija reflektorskih svjetiliki na stubovima rasvjete je 65
stepeni u odnosu na horizontalnu ravan poda.

10. Refleksije podnih povr§ina maksimalno 20%.

11. Refleksije zidova objekata maksimalno 50%.

12. Zbog uticaja stubova portala u postrojenjima, iste je potrebno tretirati u
proracunu. Zbog njihove reSetkaste prirode i uticaja na distribuciju svijetla,
iste formirati kao "prozirne" (transparent) sa refleksijom ne ve¢om od 50%

J. .. N | ot ' (reflection factor) i propustom ne veéim od 40% (degree of transmission).

H

O
T
I
o=
o)

13. Komplet rasvjetu postrojenja treba dizajnirati na nacin da postoje dva nivoa
ob o osvijetljaja, tj dvije zone paljenja.
S STAZA - ¢ © T N S e . 14. Zona 1, osnovni nivo ima slede¢e potrebe u pogledu srednjeg nivoa
o \ s e L osvjetljaja i ravnomjernosti:
_ o o . Ulazna kapija - Em >20Ix i Uo >0.4
) o . o L Ulazni koridor - Em >10Ix i Uo >0.4
. ~ > I I I N I 3 . Ostale Staze/Koridori - Em >10Ix i Uo >0.2
H=25m+0.8m ograda | 4 - o g Perimetri - Em >5Ix i Uo >0.2
§ ’ g Transformatori (ETR) - Em >15Ix i Uo >0.4
- Postrojenja (RP) 400kV i 110kV - Em > 20Ix i Uo >0.2
15. Zona 2, maksimalni nivo ima sledece potrebe u pogledu srednjeg nivoa
. osvjetljaja i ravnomjernosti:
'U oo . -U . 2 5 —U Ulazna kapija - Em >30Ix i Uo >0.4
= 3 Ulazni koridor - Em >20Ix i Uo >0.4
O : O : O Ostale Staze/Koridori - Em >30Ix i Uo >0.2
(@) N - [¢)) Perimetri - Em >10Ix i Uo >0.2
_I _I _I Transformatori (ETR) - Em >50Ix i Uo >0.4
m : ;U : m Postrojenja (RP) 400kV i 110kV - Em > 50Ix i Uo >0.4
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NAPOMENA:

e OVAJ CRTEZ JE U VLASNISTVU PREDUZECA CGES | NE SMIJE SE NI U SEGMENTIMA, NI U CJELOSTI
REPRODUKOVATI ILI KOPIRATI.

e SVE MJERE PROVJERITI NA LICU MJESTA, A SVAKO ODSTUPANJE OD PROJEKTA PRIJAVITI INVESTITORU.
DIMENZIJE SE NE SMIJU SKALIRATI/MIJENJATI.

a8 H=25m+0.8m ograda

(m)
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